FIELD INSPECTION & MAINTENANCE REPORT

Water Main Break Investigation — Apache Trail

Apache Junction Water System  ·  Arizona Water Company

| Asset ID | SEG-00347 | Asset Type | Distribution Main (Cast Iron, 8-inch) |
| --- | --- | --- | --- |
| Location | Apache Trail near Idaho Rd, Apache Junction | Inspection Date | 2026-05-02 |
| Inspector | Diane Foster | System | Apache Junction |
| Condition Rating | Poor (2/5) | Report Status | Submitted |

Findings

48-year-old cast iron main failed at a circumferential crack.

Estimated 12,000 gallons lost before isolation.

Soil conditions show corrosive backfill contributing to external corrosion.

Two customer service connections temporarily affected; service restored within 6 hours.

Elevated turbidity observed downstream during repair — flushing performed.

Condition Assessment

The distribution main (cast iron, 8-inch) exhibits significant deterioration that warrants prioritized repair or replacement. Continued operation without intervention risks service disruption to the Apache Junction system.

Recommended Actions

Replace the failed segment with ductile iron and cathodic protection.

Prioritize this segment in the FY2027 main replacement program.

Coordinate with Water Quality Division on post-repair turbidity follow-up given the system's current WARNING status.

Survey adjacent cast iron segments of similar vintage.

Report filed by Diane Foster, AWC Field Operations. This inspection record is an internal operational document. Asset condition data feeds the AWC capital planning and maintenance scheduling process.