FIELD INSPECTION & MAINTENANCE REPORT

Storage Tank T-03 Structural Inspection

Sierra Vista Water System  ·  Arizona Water Company

| Asset ID | AST-0031 | Asset Type | Storage Tank (500,000 gal) |
| --- | --- | --- | --- |
| Location | Fry Blvd Reservoir Site, Sierra Vista | Inspection Date | 2026-03-27 |
| Inspector | Raymond Ortiz | System | Sierra Vista |
| Condition Rating | Fair (3/5) | Report Status | Submitted |

Findings

Exterior coating shows moderate UV chalking on the south-facing panels.

No structural deformation or leakage detected.

Cathodic protection anode at 40% remaining life.

Overflow screen intact; vent screen requires cleaning.

Condition Assessment

The storage tank (500,000 gal) shows moderate wear consistent with its age. It remains serviceable but should be monitored and scheduled for preventive maintenance within the next budget cycle.

Recommended Actions

Schedule exterior recoating within 18 months.

Replace cathodic protection anode at next drain-down.

Clean vent and overflow screens this quarter.

Report filed by Raymond Ortiz, AWC Field Operations. This inspection record is an internal operational document. Asset condition data feeds the AWC capital planning and maintenance scheduling process.